## Slide 1: Gated spillways - are they safe enough?
.,,
1
Bryan Leyland
MSc, FIEE, FIMechE, FIPENZ
Leyland Consultants
New Zealand

## Slide 2: Safety considerations
Failures of large dams have drowned thousands of people
The hydro industry has no universally accepted and monitored safety standards
Accidents and near accidents are not reported and analysed
Gate safety is seldom analysed
  many designers believe that the operators are primarily responsible for safe operation

## Slide 3: Spillway Safety
  About 30% of dam failures are caused by gate failure
    at least 7 dams have failed..
  Many gate systems can be totally disabled by
    power supply failure
    control system failure
    operator error
Many gate systems have a 1:100 probability of failure
It should be >1:10,000

## Slide 4: Spillway options
Overspill - no risk of failure
Float operated gates - very low risk
Flap gates - low risk - open without power
Radial gates - high risk - power needed for opening
  range of lifting systems - some better than others

## Slide 5: TOPS gate
www.amanziflow.co.za

## Slide 6: Radial gate
An external power supply is needed to open the gate
The cylinder is long and expensive
  If it seizes up the gate cannot be opened
If a hose fails the gate cannot be opened

## Slide 7: Gates that need power to open
A single event should not result in failure
  Redundant reliable power supply
  Diesels..
      battery must be ok
      tank full of clean fuel
      cooling system serviceable
  Redundant control system
  Open automatically if operators are absent

## Slide 8: Ross River Dam - Australia

## Slide 9: 5 diesels for 3 gates!

## Slide 10: Main and backup lifting gear
One set is conventional
The backup set does not need an outside power supply or operator intervention

## Slide 11: Alternative lifting gear

## Slide 12: Sayano Shusenskaya accident
6400 MW
Concrete arch-gravity dam 242 m high
Crest length 1074 m
Power station was flooded

## Slide 13: 6400 MW station
The accident happened at 8:13:25 local time
75 lives were lost
Single gantry crane lifts
all 11 spillway gates
Supply to the single gantry crane was lost
Emergency arrangements were made in time

## Slide 14: If the Dam had Failed..
The 300 MW Maynskaya Hydro would have been destroyed in a matter of minutes
An hour or so later the town ofSayanogorsk would be flooded - more than 200,000 people at risk.
The 6000 MW Krasnoyarsk dam would have been overtopped
If it failed, Krasnnoyarsk city would have been flooded

## Slide 15: Banqiao Dam Failure - China
It should have had more spillway gates
  Banqiao dam in China failed in 1975
  and killed >175,000 people

## Slide 16: Machhu 2 failure 1979 - India
2000-10,000 died

## Slide 17: Kentucky Dam USA
Two gantry cranes to lift 24 gates!

## Slide 18: Recent experience
I was a member of a Dam Safety Panel for a dam in Africa
  responsible for gate safety
The design included 14 - 6m x 6m radial gates
  the previous consultant had recommended 6 m high flap gates
I said that the radial gates were too risky
  recommended flap gates - cheaper, safer and more flood capacity
The Panel President insisted that the radial gates were safe
  I resigned

## Slide 19: Failure modes
X
X
X
X
X

## Slide 20: What can be done?
Modern health and safety legislation requires
  avoid risks or manage those that cannot be avoided
  adapt working conditions, equipment and methods taking into account development in techniques

## Slide 21: What are the implications?
An engineer must
  examine the safety implications of his design
  assess the risks of his design and alternatives
  choose the design that offers the least risk at a reasonable price
  record the results of his evaluation and, if a major safety issue is involved, get it peer reviewed
If this is not done and an accident occurs, the engineer could face very serious charges including manslaughter

## Slide 22: What else could be done?
Set up an international organisation that obliges all designers and operators of large dams to:
  adhere to an agreed set of safety standards
  review designs in accordance with the standards
  report all failures and near failures so that, if necessary, the safety standards can be amended
If this is done, dam safety will approach the safety standards of aeroplanes and nuclear stations that are already much safer than hydro dams
If it is not done, the risk of another major dam failure killing thousands of people will remain

## Slide 23: Summing up
Large dams
  store huge amounts of energy
  cannot be abandoned
  decommissioning is virtually impossible
  will be a risk to future generations for the forseeable future
Gates are a major risk factor