## MASTER
Hydro scheme data and cost estimates |  |  |  |  | SS1aHydro scheme data and cost estimates.xlsx
|  | Bryan Leyland Consulting Engineer | [7 empty] | JOB NAME: | Example |  | Printed: | 42355.7874
[10 empty] | JOB NUMBER: | 0 |  |  | 2019-12-18 18:54
Scheme name |  | Purua | [7 empty] | DESCRIPTION: | Trial
Printed
2019-12-18 18:54
42355.7874
| Description |  |  | 1 set | 2 sets |  | Scheme
|  | Item | Rate | 2890kW | 3130kW | 1920kW | 21330kW | 21050kW
Headworks | [9 empty] | Canal water velocities and slopes
| Flow | m3/s |  | 22 | 24 | 0.8 | 9 | 9 |  | Material | Sideslope v:h | max vel m/s
| Annual average diverted flow |  |  | 9.5 | 10 | 0.48 | 4 | 5 | note | Sand | 1:3 | 0.4
| Reservoir or headpond full level |  |  | 80.5 | 80.5 | 300 | 300 | 300 |  | Sandy earth | 1:2 | 0.6
| Reservoir Minimum operating level (not used in calcs) | m |  | 80 | 80 | 290 | 290 | 290 |  | Clay/earth | 1:1.5 | 0.8
| Turbine CL Level |  |  | 64 | 64 | 2 | 2 | 2 |  | Clay | 1:1 | 1.2
| Normal tailwater level |  |  | 64.5 | 64 | 2.5 | 2.5 | 2.5 |  | Bricks/masonry | 1.5:1 or vertical | 1.5
Canal | [9 empty] | Concrete | 1.5:1 or vertical | 2
| Length |  |  | 200 | 200 | 1200 | 1200 | 1200 |  | Plastic lining | Depends on | 1.5-2
| Depth d | m |  | 4 | 4 | 0.55 | 1.54 | 1.54 |  |  | foundation |  |  |  | walking probably go for six yes just spreadsheet come back to the love of your was reverse engineer will be done is yet no object change fix which
| Bottom width b | m |  | 8 | 8 | 0.9 | 1.52 | 1.52
| Side slope | deg |  | 45 | 45 | 30 | 30 | 30 |  | Manning's n | Approx value
| Manning's n |  |  | 0.025 | 0.025 | 0.02 | 0.02 | 0.02 |  | Concrete - smooth | 0.02
| Slope | m/m |  | 4e-05 | 5e-05 | 0.001 | 0.001 | 0.001 |  | Masonry | 0.015
| Area | m2 |  | 47.9282 | 47.9282 | 1.0174 | 6.4389 | 6.4389 |  | Earth - good | 0.025
| Hydraulic radius | m |  | 2.4853 | 2.4853 | 0.32869 | 0.83965 | 0.83965 |  | Earth - rough | 0.03
| Flow that the canal can carry | m3/s |  | 22.2903 | 24.9214 | 0.76768 | 9.0789 | 9.0789 |  | Rock | 0.035
| Velocity (must not be too high for linnig) | m/s |  | 0.45902 | 0.50075 | 0.7863 | 1.3978 | 1.3978
| Wetted volume of excavation | m3 |  | 9585.6333 | 9585.6333 | 1220.9046 | 7726.6575 | 7726.6575
| Headloss | m |  | 0.008 | 0.01 | 1.2 | 1.2 | 1.2 | note
HDPE up to 200 m
| Length | m |  | 100 | 100 | 800 | 800 | 800
| Diameter OD | mm |  | 3500 | 2500 | 700 | 1500 | 1400
| Average head |  |  | 20 | 20 | 100 | 100 | 100
| Number |  |  | 1 | 2 | 1 | 1 | 1
| Pressure thickness (for average head) | mm |  | 43.7603 | 31.2574 | 43.7603 | 93.7721 | 87.5206
| Assumed average thickness | mm |  | 20 | 20 | 25 | 25 | 25 | Insert standard thicknesses
| Weight | Tonnes |  | 21.5985 | 30.8357 | 43.1781 | 92.7093 | 86.5071
| Water velocity | m/s |  | 2.3398 | 2.5248 | 2.4109 | 5.4502 | 6.2876 |  | Hazen
| Hazen Williams C |  |  | 140 | 140 | 140 | 140 | 140 |  | Williams C
| Friction head loss | m |  | 0.084824 | 0.14514 | 5.0016 | 8.9215 | 12.6309 |  | Cast iron | 100
High press steel penstocks | [9 empty] | Cement lining | 130
| Length | m |  | 70 | 70 | 1000 | 1000 | 1000 |  | Concrete | 120
| Calculated diameter | m |  | 4279.1923 | 3301.9357 | 543.3304 | 1542.4704 | 1547.2422 |  | GRP | 150
| Diameter adopted | mm |  | 3500 | 2500 | 600 | 1500 | 1500 |  | HDPE | 140
| Number |  |  | 1 | 2 | 1 | 1 | 1 |  | Painted steel | 140
| Pressure thickness (at lower end) | mm |  | 12 | 10 | 5.4291 | 13.5728 | 13.5728 |  | Unpainted steel | 100
| Assumed thickness |  |  | 12 | 10 | 6.5 | 6.5 | 6.5 | Insert chosen thickness with corrosion allowance
| Weight | Tonnes |  | 78.5084 | 93.4624 | 104.1438 | 260.3595 | 260.3595
| Water velocity | m/s |  | 2.3183 | 2.4842 | 2.9561 | 5.1824 | 5.1824
| Hazen Williams C |  |  | 130 | 130 | 130 | 130 | 130
| Friction head loss | m |  | 0.0666 | 0.11204 | 11.7773 | 11.3165 | 11.3165
| Penstock total loss | m |  | 0.15142 | 0.25718 | 16.779 | 20.238 | 23.9474
Powerhouse/Plant
| Turbine CL (Pelton) | m |  | 64 | 64 | 2 | 2 | 2
| Tailwater level | m |  | 64 | 64 | 0 | 0 | 0
| Powerhouse floor level | m |  | 65 | 65 | 1.5 | 1.5 | 1.5
| Flow | m3/s |  | 22 | 24 | 0.8 | 9 | 9
| Gross head | m |  | 16.5 | 16.5 | 298 | 298 | 298
| Total headloss excl canal +1 m for inlet and outlet | m |  | 1.1514 | 1.2572 | 17.779 | 21.238 | 24.9474
| Headloss % of gross head |  |  | 6.9783 | 7.6192 | 5.9661 | 7.1268 | 8.3716
| Nett head Hn | m |  | 15.3486 | 15.2428 | 280.221 | 276.762 | 273.0526
| No of Turbines |  |  | 1 | 2 | 1 | 1 | 1
| Turbine type(P =Pelton or R= reaction (Kaplan or Francis) |  |  | r | r | P | P | P
| Speed | rpm |  | 375 | 428 | 1500 | 1500 | 1500 | Not used in calcs
| Efficiency | % |  | 0.92 | 0.92 | 0.92 | 0.92 | 0.92
| Turbine rating | kW |  | 3044.4207 | 3298.3033 | 2021.1784 | 22457.5763 | 22156.5788
| Total generator output (eff=0.95) | kW |  | 2890 | 3130 | 1920 | 21330 | 21050
| Generator rating @ 0.9 pf | kVA |  | 3211.16 | 1738.94 | 2133.38 | 23700.05 | 23388.94
| Generator voltage | kV |  | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | Not used in calcs
Transmission/Distribution
| Transformer rating | kVA |  | 3200 | 3500 | 2200 | 23900 | 23600
| No of Transformers |  |  | 1 | 1 | 1 | 1 | 1 | Not used in calcs
| Trans line length | km |  | 10 | 10 | 5 | 5 | 5
| Voltage | kV |  | 33 | 33 | 11 | 11 | 11 | Not used in calcs
| kW sent out (incl TF loss) | kW |  | 2872.66 | 3111.22 | 1908.48 | 21202.02 | 20923.7
COSTS $000
Intake and penstocks
| Civil works - weir and pond | Estimate |  | 200 | 100 | 100 | 100 | 100
| Intake | Estimate |  | 200 | 110 | 120 | 120 | 120
| Canal | $/m3 | 20 | 100 | 191.7127 | 24.4181 | 154.5331 | 154.5331 | Estimates can be obtained from local contractors
| HDPE penstocks | $/tonne. | 3000 | 64.7954 | 92.5072 | 129.5343 | 278.1278 | 259.5213 | Estimates can be obtained from local fabricators
| Steel penstocks | $/tonne. | 10000 | 785.084 | 934.6238 | 1041.438 | 2603.5949 | 2603.5949 | Estimates can be obtained from local fabricators
| Civil works and installation | $/m |  | 200 | 250 | 555 | 555 | 555
| Total |  |  | 1549.8794 | 1678.8437 | 1970.3904 | 3811.2559 | 3792.6493
Civil
| Access roading | Estimate |  | 50 | 50 | 100 | 100 | 100
| Powerhouse | Estimate |  | 700 | 800 | 300 | 300 | 300
| Civil total |  |  | 750 | 850 | 400 | 400 | 400
Powerhouse Plant
| Cost factor Kc (Cost = Kc*((kW/1000)^0.7)/(Hn^0.3) |  |  | 3000 | 3000 | 5000 | 5000 | 5000 | Kc is calculated from a known similar scheme
| Calculated Turbine, IV and generator cost |  |  | 2779.2609 | 3625.6982 | 873.3371 | 4729.1481 | 4704.6123 |  | Known cost $000 | 1500
| Turbine (enter zero to use calculated cost) |  |  | 0 | 0 | 0 | 0 | 100 |  | Power kW | 2000
| Inlet valve |  |  | 0 | 5 | 5 | 5 | 5 |  | Nett head Hn | 200
| Generator |  |  | 0 | 0 | 50 | 50 | 50 |  | Factor Kc | 4525.6323
| Turbine Inlet valve and Generator generator cost |  |  | 2779.2609 | 3625.6982 | 873.3371 | 4729.1481 | 155 | Insert known data in green cells
| PLC & Control gear |  |  | 75 | 100 | 75 | 75 | 75
| SCADA, metering & communication |  |  | 20 | 25 | 50 | 50 | 50
| LV Switchgear & protection |  |  | 15 | 25 | 25 | 25 | 25
| HV & LV cabling |  |  | 50 | 60 | 50 | 50 | 50 |  | 3.06
| Crane & misc mech, pumps etc |  |  | 60 | 70 | 60 | 60 | 60
| Erection & commissioning etc |  |  | 200 | 300 | 200 | 200 | 200
| Machinery Total |  |  | 3199.2609 | 4205.6982 | 1333.3371 | 5189.1481 | 615
Transmission
| Trans line cost (installed) | $/km | 40000 | 400 | 400 | 200 | 200 | 200
| MV (11-20 kV) Switchgear |  |  | 0 | 10 | 10 | 10 | 10
| HV (33-132 kV) Switchgear |  |  | 25 | 25 | 0 | 0 | 0
| Main Transformer |  |  | 200 | 200 | 25 | 25 | 25
| Auxiliary Transformer |  |  | 20 | 20 | 0 | 0 | 0
| transport and Installation |  |  | 20 | 20 | 20 | 20 | 20
| Transmission Total |  |  | 665 | 675 | 255 | 255 | 255
Project Totals
| Land, easements |  |  | 50 | 50 | 50 | 50 | 50
| Intake and penstocks |  |  | 1549.8794 | 1678.8437 | 1970.3904 | 3811.2559 | 3792.6493
| Roads and powerhouse |  |  | 750 | 850 | 400 | 400 | 400
| Contingency for land, penstocks & civil etc |  | 20% | 469.9759 | 515.7687 | 484.0781 | 852.2512 | 848.5299
| Machinery |  |  | 3199.2609 | 4205.6982 | 1333.3371 | 5189.1481 | 615
| Transmission |  |  | 665 | 675 | 255 | 255 | 255
| Contingency for M&E |  | 15% | 579.6391 | 732.1047 | 238.2506 | 816.6222 | 130.5
| Sub Total |  |  | 7263.7554 | 8707.4154 | 4731.056 | 11374.2773 | 6091.6792
| Design, proj mgmt & supervision |  |  | 100 | 100 | 100 | 100 | 100
Total |  |  |  | 7363.7554 | 8807.4154 | 4831.056 | 11474.2773 | 6191.6792
Financial return |  | $000
| $000/kW Total |  |  | 2.548 | 2.8139 | 2.5162 | 0.53794 | 0.29414
| Average output | kW |  | 1240.4668 | 1296.3417 | 1145.088 | 9423.12 | 11624.2778
| Annual MWh |  |  | 10866.4893 | 11355.953 | 10030.9709 | 82546.5312 | 101828.6733
| $000/MWhpa |  |  | 677.6573 | 775.5769 | 481.614 | 139.0037 | 60.8049
| Income @ | $/kWh | 0.1 | 1086.6489 | 1135.5953 | 1003.0971 | 8254.6531 | 10182.8673
| Income @ | $/kWh | 0.12 | 1303.9787 | 1362.7144 | 1203.7165 | 9905.5837 | 12219.4408
| Income @ | $/kWh | 0.14 | 1521.3085 | 1589.8334 | 1404.3359 | 11556.5144 | 14256.0143
| O&M |  |  | 50 | 50 | 50 | 50 | 50
| Capital charges 8% |  | 8% | 589.1004 | 704.5932 | 386.4845 | 917.9422 | 495.3343
| Capital + O&M |  |  | 639.1004 | 754.5932 | 436.4845 | 967.9422 | 545.3343
| Annual surplus | $/kWh | 0.1 | 447.5485 | 381.0021 | 566.6126 | 7286.7109 | 9637.533
| Annual surplus | $/kWh | 0.12 | 664.8783 | 608.1211 | 767.232 | 8937.6416 | 11674.1065
| Annual surplus | $/kWh | 0.14 | 882.2081 | 835.2402 | 967.8514 | 10588.5722 | 13710.6799
| Return on scheme cost | $/kWh | 0.1 | 6.078% | 4.326% | 11.73% | 150.8% | 199.5%
| Return on scheme cost | $/kWh | 0.12 | 9.029% | 6.905% | 15.88% | 185% | 241.6%
| Return on scheme cost | $/kWh | 0.14 | 11.98% | 9.483% | 20.03% | 219.2% | 283.8%
Note on E4: Insert data in green shaded cells only!
Note on K12: Average flow is estimated or calculated from flow/duration curvis
Note on K29: Headloss: Adjust Slope and canal dimensions without exceeding allowable velocity for the material flow? = mismatch >5%